## Project
Project name | Sample Plant (invented data)
Code (IEC or IS) | IEC
Prepared by | Manas Mohanty

## Cables
tag | phase | voltage_v | design_current_a | load_kw | power_factor | length_m | conductor | insulation | method | cores | ambient_c | grouped_circuits | vd_limit_pct | fault_current_ka | fault_time_s | device_rating_a | soil_resistivity_kmw
F-01 Pump motor | 3ph | 415 |  | 22 | 0.85 | 60 | Cu | PVC | C | 3 | 40 | 2 | 5 | 5 | 0.1 | 50
F-02 Yard lighting | 1ph | 230 | 10 |  | 0.9 | 95 | Cu | PVC | B1 | 2 | 35 | 2 | 3 | 1 | 0.1 | 16
F-03 Board tail | 3ph | 415 | 40 |  | 0.9 | 10 | Cu | XLPE | E | 3 | 30 | 1 | 5 | 25 | 0.4 | 50
F-04 Store building | 3ph | 415 | 150 |  | 0.85 | 150 | Al | XLPE | D2 | 3 | 30 | 2 | 5 | 10 | 0.3 | 160
F-05 Main incomer | 3ph | 415 | 600 |  | 0.9 | 40 | Cu | PVC | C | 3 | 40 | 3 | 5 | 25 | 0.4 | 630

## Guide
Column | Unit | What to enter
tag | - | Cable reference, e.g. F-01. Required.
phase | - | 1ph or 3ph.
voltage_v | V | Line voltage for 3ph (e.g. 415), phase voltage for 1ph (e.g. 230).
design_current_a | A | Design current Ib. Leave blank to calculate it from load_kw.
load_kw | kW | Used only when design_current_a is blank.
power_factor | - | Between 0 and 1, e.g. 0.85.
length_m | m | Route length, one way.
conductor | - | Cu or Al.
insulation | - | PVC or XLPE.
method | - | Installation method: A1, A2, B1, B2, C, E, D1, D2. Each is described in the Installation methods list below.
cores | - | LOADED conductors: 2 for 1ph, 3 for 3ph (a 4-core 3ph cable is entered as 3).
ambient_c | deg C | Air temperature; for D1 and D2 the ground temperature. Between table rows, the next higher row is used.
grouped_circuits | - | Number of circuits in the group, including this one. 1 if alone.
vd_limit_pct | % | Permitted voltage drop, e.g. 5.
fault_current_ka | kA | Prospective fault current at the cable.
fault_time_s | s | Disconnection time of the protective device for that fault.
device_rating_a | A | Rating In of the overload device. Leave blank if there is none.
soil_resistivity_kmw | K.m/W | D1 and D2 only. Leave blank for 2.5.
Installation methods |  | Where the cable runs, and the grouping factors used
A1 |  | Single-core cables or insulated conductors in conduit in a thermally insulated wall. Grouping: bunched or enclosed (Table 36 item 1).
A2 |  | Multi-core cable in conduit in a thermally insulated wall. Grouping: bunched or enclosed (Table 36 item 1).
B1 |  | Single-core cables or insulated conductors in conduit or trunking on a wall, less than 0.3 x conduit diameter from it. Grouping: bunched or enclosed (Table 36 item 1).
B2 |  | Multi-core cable in conduit on a wall, less than 0.3 x conduit diameter from it. Grouping: bunched or enclosed (Table 36 item 1).
C |  | Single-core or multi-core cable fixed on a wall, less than 0.3 x cable diameter from it; also used for cable on unperforated tray and cable direct in masonry. Grouping: single layer on wall, floor or unperforated tray (Table 36 item 2).
E |  | Multi-core cable in free air, at least 0.3 x cable diameter clear of any surface, for example on perforated tray, brackets or ladder. Grouping: single layer on perforated tray (Table 36 item 4).
D1 |  | Multi-core cable in ducts in the ground (reference: 100 mm duct, 0.7 m deep). Grouping: ducts touching (Table 38).
D2 |  | Cable laid direct in the ground (reference: 0.7 m deep). Grouping: cables touching (Table 37).